## Slide 1: 6LoBAC: A new IPv6 Data Link
Kerry Lynn
<kerlyn@ieee.org>
15 December 2015

## Slide 2: IoT Background

## Slide 3: Review (Layered Model)
source A
source B
source C
dest. A
dest.B
dest. C
HTTPS
COAPS
TCP/TLS
UDP/DTLS
IPv6
6LoWPAN
802.15.4
Other
802.3
Application
Transport
Inter/network
Data Link
(MAC/PHY)
Notes: Network engineers think in “layers”
Each layer generally has a service interface and protocol header

## Slide 4: Goal
Develop a low-cost wired IPv6 solution for commercial building control applications

## Slide 5: Technical Approach
Leverage elements of 6LoWPAN solution [RFCs 4944, 6282, 6775]
Minimize changes to existing MS/TP specification [BACnet Clause 9]
Goal: co-existence with legacy MS/TP nodes
  No changes to frame header format, control frames, or MS/TP Master Node state machine
MS/TP Extended Frames proposal includes:
  New frame type for IPv6 (LoBAC) Encapsulation
  Larger MSDU (1500+ octets)
  32-bit FCS (CRC-32K)
  COBS (Consistent Overhead Byte Stuffing) encoding
Notes: - Top-down design, bottom-up implementation

## Slide 6: MS/TP Background
BACnet is the ISO/ANSI/ASHRAE [Standard 135-2012] data communication protocol for Building Automation and Control networks
MS/TP (Master-Slave/Token-Passing) is a widely used data link defined in BACnet
  Based on RS-485 single twisted pair PHY; supports data rates up to 115.2 kpbs and 1 km diameter
  Contention-free MAC (token passing bus)
  Consider it a wired alternative to IEEE 802.15.4

## Slide 7: MS/TP Extended Frame Format
Data CRC (CRC-32K, LS octet first, COBS Encoded)
COBS Encoded Data (1 – 1500 octets before encoding)
0x55
0xFF
FrameType
0
31
SrcAddr
Length (MS octet first)
HeaderCRC
Frame Type: 34 = IPv6 (LoBAC) Encapsulation
Destination Address: 0 – 127, 255 (all nodes)
Source Address: 0 – 127
DestAddr
Optional 0xFF
…
…

## Slide 8: CRC Background
Encoder
Decoder
Noisy Channel
Noisy channel acts like a random bit mask XOR’d
with the data word
We use cyclic redundancy code (CRC) to detect
these errors
Data word (frame) is divided by a polynomial G(x);
remainder is CRC
Detection capability is related to size and co- efficients of G(x)

## Slide 9: COBS Encoding Basics
Code | Followed By | Meaning
0x00 | (not applicable) | (not allowed)
0x01 | nothing | A single zero byte
0x02 | one data byte | The single data byte, followed by a zero byte
1 ≤ n ≤ 253 | (n – 1) data bytes | The (n – 1) data bytes, followed by a zero byte
0xFF | 254 data bytes | The 254 data bytes, not followed by a zero byte
x
y
z
...
z
y
00
x
00
x
y
00
FF
x
y
z
...
y
01
03
x
y
02
x





## Slide 10: COBS Encoding in Detail
"Phantom zero" is appended to input to resolve ambiguity in final code block:
H
e
l
l
o
H
e
l
l
o
00
06
H
e
l
l
o
06


H
e
l
l
o
01
COBS overhead:
  At least, one octet per field
  At most, one octet per 254 (6 octets per 1500;
  ≈ 0.4%)
An arbitrary octet (e.g. 0x55) may be removed by XOR-ing it over the COBS encoder output stream

## Slide 11: 6Lo Background
Need to define encapsulation
Need to define mapping of MAC address for:
  Interface Identifier (IID)
  Stateless Address Auto-Configuration (SLAAC)
  Unicast and multicast transmission
Header compression
Security Considerations
Other (e.g. abstract MAC interface)

## Slide 12: LoBAC Encapsulation
Uses 6LoWPAN Dispatch Header [RFC 4944]:
1 2 3
0 1 2 3 4 5 6 7 8 9 0 1 2 3 4 5 6 7 8 9 0 1 2 3 4 5 6 7 8 9 0 1
+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+
|0 1| Dispatch | Type-specific header
+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+
Pattern | Header Type
00 XXXXXX | NALP – Not a LoWPAN (LoBAC) frame
01 000000 | ESC – Additional Dispatch octet follows
01 000001 | IPv6 – Uncompressed IPv6 header
... | Reserved by RFC 4944
01 1XXXXX | LOWPAN_IPHC – Compressed IPv6 header

## Slide 13: LoBAC Encapsulation (cont.)
No mesh, broadcast, or fragmentation headers
  Two options remain:
IPv6 Dispatch
IPv6 Header
Payload
A LoBAC encapsulated IPv6 datagram
IPHC Dispatch
IPHC Header
Payload
A LoBAC encapsulated LOWPAN_IPHC
[RFC 6282] compressed datagram

## Slide 14: IPHC Compression [RFC 6282]
Assumes some 6LBR-like behavior, e.g. 6LoWPAN Context Option (6CO, [RFC 6775])
Uses 6LoWPAN short address format, formed by appending 8-bit MS/TP address to the octet 0x00
  For example, an MS/TP node with a MAC address of 0x4F results in the following IPHC short address:
|0 1|
|0 5|
+----------------+
|0000000001001111|
+----------------+

## Slide 15: IPv6 Link Local Address
The IPv6 link-local address [RFC 4291] for an MS/TP interface is formed by appending the Interface Identifier (defined in previous slide) to the prefix FE80::/64:
10 bits 54 bits 64 bits
+----------+-----------------------+----------------------------+
|1111111010| (zeros) | Interface Identifier |
+----------+-----------------------+----------------------------+

## Slide 16: Unicast Address Mapping
The Source/Target Link-Layer Address option has the following form when the link layer is MS/TP and the addresses are 8-bit MS/TP MAC addresses:
0 1 Option fields:
0 1 2 3 4 5 6 7 8 9 0 1 2 3 4 5
+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+ Type:
| Type | Length=1 | 1 = Source Link-layer address
+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+ 2 = Target Link-layer address
| |
+ Padding + Length:
| (all zeros) | The value of this field is
+ +-+-+-+-+-+-+-+-+ 1 for 8-bit MS/TP addresses
| | MS/TP Address |
+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+-+ MS/TP Address:
The 8-bit MAC address in
canonical bit order

## Slide 17: Multicast Address Mapping
MS/TP only supports link-local broadcast
Uses 6LoWPAN short address format, formed by appending 0xFF to the octet 0x00
  All IPv6 multicasts on the MS/TP link map to the following IPHC short destination address:
|0 1|
|0 5|
+----------------+
|0000000011111111|
+----------------+

## Slide 18: Summary
6LoBAC was the first to propose re-use of 6LoWPAN solutions (RFCs 4944, 6282, 6775)
Served as a pattern for subsequent proposals (Z-Wave, BTLE, NFC, etc.) resulting in formation of the IETF 6lo working group
Remains the only wired 6lo PHY
Has passed ETSI Interoperability Plugtest
About to enter WG “last call”

## Slide 19: Thank You
Questions?